## Thora Addl DTC
CHAMUNDESHWARI ELECTRICITY SUPPLY CORPORATION LIMITED
Estimate No: Date:
Estimate for providing |  | additional 25 KVA DTC to improve the voltage to Thora village
, Kedemalluru GP coming under O&M Section Virajpet,Virajpet Subdivision.
Part : A -Extension of HT line
5.856 | Rabbit ACSR Average span length | 0.032 | No of Spans |  | 61 | No of wires | 3
Sl No | PARTICULARS | UNIT | QTY | RATE | AMOUNT | LABOUR CHARGES
[6 empty] | RATE | AMOUNT
1 | 9mtr long Rcc pole DP stucture as per cost data sheet no 15 | Set | 1 | 56161 | 56161 | 6989 | 6989
2 | Rcc pole 9 mtr long | Nos | 12 | 7153 | 85836 | 1341 | 16092
3 | Psc pole 9mtr long | Nos | 48 | 4276 | 205248 | 1341 | 64368
4 | Rcc pole 8 mtr long | Nos | 0 | 5306 | 0 | 1072 | 0
5 | Psc pole 8mtr long | Nos | 8 | 3578 | 28624 | 1072 | 8576
6 | Special Cross Arm with Cross Arm for EG Stirrups, | Set | 0 | 1503 | 0 | 400 | 0
7 | 11 kV, Horizontal Cross Arm with clamps, HTST supports, bolts, nuts For RCC | Set | 12 | 668 | 8016 | 122 | 1464 | 1.952
8 | 11 kV, Horizontal Cross Arm with clamps, HTST for PSC | Set | 60 | 664 | 39840 | 122 | 7320
9 | L.T.4 Pin cross arms, with pole clamps, bolts, nuts and washers (for RCC poles) | Set | 12 | 439 | 5268 | 112 | 1344
10 | L.T.4 Pin cross arms, with pole clamps, bolts, nuts and washers (for PSC poles) | Set | 50 | 435 | 21750 | 112 | 5600
11 | 11 kV, 45 KN Disc Polymeric Insulator | Nos | 66 | 202 | 13332 | 0 | 0
12 | 11 kV, 5 KN Polymeric Pin Insulator | Nos | 216 | 221 | 47736 | 0 | 0
13 | No 8 Strain Insulator | Nos | 24 | 25 | 600 | 0 | 0
14 | 1.1 kV Pin Insulator with GI Pin | Nos | 100 | 65 | 6500 | 0 | 0
15 | Rabbit conductor | Kms | 5.9438 | 61515 | 365635.3176 | 3299 | 19608.7282
16 | Conductor accessories @ 3% |  |  |  | 10969.0595 |  | 0
17 | PG Clamps for Rabbit conductor | Nos | 66 | 116 | 7656 | 0 | 0
18 | Guy Set Complete with No. 15 Strain Insulator & Concreting materials | Set | 18 | 1209 | 21762 | 448 | 8064
19 | Guy concreting with Boulders, Mud and Sand | Nos | 18 | 0 | 0 | 200 | 3600
20 | Spiral earth eletrode | Nos | 60 | 248 | 14880 | 70 | 4200
21 | EG Stirrups with GI wire lacing | Set/2 No | 60 | 287 |  | 125
22 | Guarding between HT & LT Line | Span | 0 | 5451 | 0 | 1462 | 0
23 | D.O.L.O Fuse | Set/3 Nos | 0 | 5672 | 0 | 178 | 0
24 | Trimming of Tree branches | Kms | 0.3 | 0 | 0 | 3881 | 1164.3
25 | Loading and unloading of 9Mtrs poles | Nos | 62 | 0 | 0 | 106 | 6572
26 | Loading and unloading of 8 Mtrs poles | Nos | 8 | 0 | 0 | 79 | 632
27 | Releasing and restriging of No 2 ACSR Condr | Kms | 4.32 | 0 | 0 | 2178 | 17877.024
28 | Misc & unforeseen |  |  |  | 86.6229 |  | 28.9478
| TOTAL |  |  |  | 939900 |  | 173500
| Material Cost |  |  |  | 939900
29 | Labour charges (a) Casual |  |  |  | 173500
| © MZ Charges @45% |  |  |  | 78075
30 | Head load charges (if applicable) |  |  |  | 0
31 | Total Labour charges |  |  |  | 251575
32 | GST@18% on Total labour Charges |  |  |  | 45283.5
33 | Contribution towards Employees Provident Fund Charges & ESI @16.25% total Labour Charges |  |  |  | 40880.9375
34 | Transportation from stores to site @ 2% on material cost |  |  |  | 18798
35 | Contingencies @ 2% on total Material & Labour cost |  |  |  | 23829.5
36 | ESCOM Establishment cost @ 20% on labour charges as applicable |  |  |  | 50315
37 | Statutory charges as per actuals(Electrical Inspectorate charges, civic body charges etc.) |  |  |  | 1000
38 | Compensation cost for tree cutting etc: as per approved norms |  |  |  | 0
39 | Any other charges if applicable |  |  |  | 0
Total cost of the estimates |  |  |  |  | 1371581.9375
CHAMUNDESHWARI ELECTRICITY SUPPLY CORPORATION LIMITED
Estimate No: Date:
Part : B -Erection of DTC
Sl No | PARTICULARS | UNIT | QTY | RATE | AMOUNT | LABOUR CHARGES
[6 empty] | RATE | AMOUNT
1 | DP Transformer Structure using RCC Pole - 9 MtrLong, 145 Kg WL | Set | 1 | 32553 | 32553 | 5205 | 5205
2 | 11 kV, 5 KN Polymeric Pin Insulator | Set | 3 | 221 | 663 | 0 | 0
3 | 11 kV, 45 KN Polymeric Insulator | Set | 3 | 202 | 606 | 0 | 0
4 | Guy Set Complete with No. 15 Strain Insulator &Concreting materials | No | 4 | 1209 | 4836 | 448 | 1792
5 | 11kv/433 V 3 phase 50 Cys 25 KVA Distribution Transformer with oil off load Tap changer (BEE-Star rated) | No | 1 | 87950 | 87950 | 863 | 863
6 | Earthing materials pipe type for grounding | Set | 3 | 1733 | 5199 | 735 | 2205
7 | Caution /Danger Board | No | 1 | 146 | 146 | 61 | 61
8 | Anti-climbing device (12mtrs /1kg G.I.Barbed wire) | No | 2 | 93 | 186 | 32 | 64
9 | concreting for Guy sets without cement | No | 4 | 0 | 0 | 200 | 800
10 | Gl wire 8 SWG | Kgs | 5 | 77.85 | 389.25 | 0 | 0
11 | Guy wire 7/10 SWG | Kgs | 10 | 80.12 | 801.2 | 0 | 0
12 | 11 KV lighting Arrester , Metal oxide, 9KV, 5KA. | set of 3 nos | 1 | 1736 | 1736 | 90 | 90
13 | LT Protection kit for 25KV DTC | No | 1 | 1651 | 1651 | 260 | 260
14 | LT wiring kit for LT protection kit (Single Circuit)
| i) Al Lead Wire - 50 Sqmm | Mtr | 25 | 79.46 | 1986.5 | 719 | 719
| ii) Heavy Duty Long Barrel Copper Lug - 50 Sq mm | No | 4 | 60 | 240
| iii) PG Clamp - Rabbit to 50 Sqmm | No | 4 | 116 | 464
| iv) Spacer for DTC Wiring | No | 8 | 41 | 328
| v) Fish Plate with necessary Clamps, bolts & | No | 2 | 229 | 458
15 | c) LT Metering box with CTs and | No | 1 | 6277 | 6277 | 650 | 650
16 | d) LT Electronic Tri-Vector Meter 5 Amps, -0.5/1.0 Accuracy Class | No | 1 | 3312 | 3312 | 798 | 798
17 | HG fuse ,11 kv solid core type (3nos) | set/3 nos | 1 | 1032 | 1032 | 178 | 178
18 | 11KV GOS, 200 A single break | No | 1 | 9125 | 9125 | 805 | 805
19 | Misc & unforeseen |  |  |  | 61.05 |  | 10
| TOTAL |  |  |  | 160000 |  | 14500
20 | Material Cost |  |  |  | 160000
21 | Labour charges (a) Casual |  |  |  | 14500
| © MZ Charges @45% |  |  |  | 6525
22 | Head load charges (if applicable) |  |  |  | 0
23 | Total Labour charges |  |  |  | 21025
24 | GST@18% on Total labour Charges |  |  |  | 3784.5
25 | Contribution towards Employees Provident Fund Charges & ESI @16.25% total Labour Charges |  |  |  | 3416.5625
26 | Transportation from stores to site @ 2% on material cost |  |  |  | 3200
24 | Contingencies @ 2% on total Material & Labour cost |  |  |  | 3620.5
25 | ESCOM Establishment cost @ 20% on labour charges as applicable |  |  |  | 4205
26 | Statutory charges as per actuals(Electrical Inspectorate charges, civic body charges etc.) |  |  |  | 1600
27 | Compensation cost for tree cutting etc: as per approved norms |  |  |  | 0
28 | Any other charges if applicable |  |  |  | 0
Total cost of the estimates |  |  |  |  | 200851.5625
CHAMUNDESHWARI ELECTRICITY SUPPLY CORPORATION LIMITED
Estimate No: Date:
0.42 | Weasel ACSR Average span length | 0.035 | No of Spans |  | 3 | No of wires | 4
Part : C -Extension of LT line |  | 0.42
Sl No | PARTICULARS | UNIT | QTY | RATE | AMOUNT | LABOUR CHARGES
[6 empty] | RATE | AMOUNT
1 | RCC Pole 9 Mtr Long. 200Kg WL | No | 0 | 7153 | 0 | 1341 | 0
2 | PSC pole 9 Mtr Long. 145Kg WL | No | 0 | 4276 | 0 | 1341 | 0
3 | RCC Pole 8 Mtr Long. | No | 0 | 5306 | 0 | 1072 | 0
4 | PCC Pole 8 Mtr Long. | No | 0 | 3578 | 0 | 1072 | 0
5 | L.T.4 Pin cross arms, with pole clamps, bolts, nuts and washers (for RCC poles) | Set | 0 | 439 | 0 | 112 | 0
6 | L.T.4 Pin cross arms, with pole clamps, bolts, nuts and washers (for PSC poles) | Set | 4 | 435 | 1740 | 112 | 448
7 | No. 8 Strain Insulators | No | 8 | 25 | 200 | 0 | 0
8 | Pin Insulators 1.1 kV class withGI Pins | No | 12 | 65 | 780 | 0 | 0
9 | Guy Set Complete (For LT) | Set | 2 | 1179 | 2358 | 448 | 896
10 | Concreting materials for guy sets without Cement | No | 2 | 0 | 0 | 200 | 400
11 | Rabbit ACSR Conductor with 1.5% Sag | Km | 0.4263 | 61515 | 26223.8445 | 3299 | 1406.3637
12 | Conductor Accessories at 3% |  |  |  | 786.7153
13 | PG Clamps for Rabbit conductor | No | 8 | 116 | 928 | 0 | 0
14 | Spiral Earth Electrode | Set | 0 | 248 | 0 | 70 | 0
15 | Loading and unloading of 8 mtr Pole | Nos | 0 | 0 | 0 | 79 | 0
16 | Loading and unloading of 9 mtr Pole | Nos | 4 | 0 | 0 | 106 | 424
17 | Misc & unforeseen |  |  |  | 0 |  | 0
| TOTAL |  |  |  | 33016.5598 |  | 3574.3637
| Material Cost |  |  |  | 33016.5598
18 | Labour charges (a) Casual |  |  |  | 3574.3637
| © MZ Charges @45% |  |  |  | 1608.4637
19 | Head load charges (if applicable) |  |  |  | 0
20 | Total Labour charges |  |  |  | 5182.8274
21 | GST@18% on Total labour Charges |  |  |  | 932.9089
22 | Contribution towards Employees Provident Fund Charges 13% & ESI @4.75 % total Labour Charges |  |  |  | 919.9519
23 | Transportation from stores to site @ 2% on material cost |  |  |  | 660.3312
24 | Contingencies @ 2% on total Material & Labour cost |  |  |  | 763.9877
25 | ESCOM Establishment cost @ 20% on labour charges as applicable |  |  |  | 1036.5655
26 | Statutory charges as per actuals(Electrical Inspectorate charges, civic body charges etc.) |  |  |  | 200
27 | Compensation cost for tree cutting etc: as per approved norms |  |  |  | 0
28 | Any other charges if applicable |  |  |  | 0
Total cost of the estimates |  |  |  |  | 42713.1324
CHAMUNDESHWARI ELECTRICITY SUPPLY CORPORATION LIMITED
30
0.42 | Weasel ACSR Average span length | 0.035 | No of Spans |  | 3 | No of wires | 4
Part : D -Decomissioning |  | 0.42
CHAMUNDESHWARI ELECTRICITY SUPPLY CORPORATION LIMITED
Part : C-Decommissioning of Old assets
Sl No | PARTICULARS |  |  | UNIT | QTY | LABOUR CHARGES
[6 empty] | RATE | AMOUNT
1 | Releasing of 8 mtr RCC/PSC Pole |  |  | Nos | 0 | 1072 | 0
2 | Releasing of 9 mtr RCC/PSC Pole |  |  | Nos | 34 | 1341 | 41034.6
3 | Releasing of No 2ACSR Conductor |  |  | Kms | 0 | 2178 | 0
4 | Releasing of HT Cross arms |  |  | Nos | 0 | 122 | 0
5 | Releasing of LT Cross arms |  |  | Nos | 34 | 112 | 3427.2
6 | Misc &unforseen | [5 empty] | 0
| Total | [5 empty] | 44461.8
7 | Material Cost |  |  |  | 0
8 | Labour charges (a) Casual |  |  |  | 44461.8
| © MZ Charges @45% |  |  |  | 20007.81
9 | Head load charges (if applicable) |  |  |  | 0
10 | Total Labour charges |  |  |  | 64469.61
11 | GST@18% on Total labour Charges |  |  |  | 11604.5298
12 | Contribution towards Employees Provident Fund Charges & ESI @16.25 % total Labour Charges |  |  |  | 10476.3116
13 | Transportation from stores to site @ 2% on material cost |  |  |  | 0
14 | Contingencies @ 2% on total Material & Labour cost |  |  |  | 1289.3922
15 | ESCOM Establishment cost @ 20% on labour charges as applicable |  |  |  | 12893.922
16 | Statutory charges as per actuals(Electrical Inspectorate charges, civic body charges etc.) |  |  |  | 200
17 | Compensation cost for tree cutting etc: as per approved norms |  |  |  | 0
18 | Any other charges if applicable |  |  |  | 0
Total cost of the estimates |  |  |  |  | 100933.7656
Part :D-Details of Released Asset
Details furnished by the field staff
Sl No | PARTICULARS | UNIT |  | QTY |  | LABOUR CHARGES
[6 empty] | RATE | AMOUNT
1 | 9 mtr PCC | Nos |  | 34 |  | Scrap N/V
2 | LT Cross arms | Nos |  | 34 |  | Scrap Iron
Year of Commission |  | 2000
Details to be furnished by the accounts staff
a)Original Value of the asset…………………….
b)Depreciation earned……………………..
a)Assesed value of the asset……………………..
Abrstract:
Part : A -Extension of HT line |  |  | 1371581.9375
Part : B -Erection of DTC |  |  | 200851.5625
Part : C -Extension of LT line |  |  | 42713.1324
Part :D-Details of Released Asset |  |  | 100933.7656
| Total |  | 1716080.398 |  | Say Rs | 1716080.398 | /-Only
(Say Rupees Seventeen Lakhs Sixteen thousand and eighty only)
Report:
This Estimate amounting to Rs. |  | 0 | /-Only | has been prepared for |  | #REF!
#REF!
●In this estimate following proposals have been made.
●Extend 11 KV OH line for Fourty one spans for a distance of |  |  |  |  | 0 | Kms using
9 mtrs long RCC/PSC poles and Rabbit ACSR Conductor as shown in the sketch.
● Provide a 25 KVA DTC using 9 Mtrs RCC DP Structure over the load center as shown in the sketch
● Provide 9 Mtrs RCC DP Structure at the tapping point as shown in the sketch
●Provide Road guarding, guy sets and stud pole wherever it is found essential.
The above said work shall be carried out under Labour contract basis and the materials will be supplied from the department stores.
This additional DTC comes on VF-2 B shetigeri Feeder from 66/33/11KV MUSS Virajpet. HT voltage regulation of the said feeder has been calculated and the calculation chart and station feasibility reports are enclosed.
At present power supply to Koka Village and surrounding area consumers are feeding from existing 63 KVA V Badaga Koka DTC whose LT extension is more and the during peak hours the tail end voltage comes down to 150 to 160volts. So it is very essential to provide an additional 25 KVA DTC to cater the load and to provide quality power supply with sufficient voltage.
Sl.no | Details | Existing |  | After providing addl DTC
|  | 63 Kva V Badaga Koka |  | 63 Kva |  | New 25 KVA DTC
|  | Circuit 1 | Circuit 2 | Circuit 1 | Circuit 2 | Circuit 1 | Circuit 2
1 | Load | 50.51 | ____ | 27.7 | ____ | 22.81 | ____
2 | LTVR | 16.95 | ____ | 0.75 | ____ | 8.95 | ____
3 | Annual Energy Loss | 2479.13 | ____ | 42.65 | ____ | 794.75 | ____
Annual Energy savings
All the necessary provision has been made in this estimate hence the estimate may kindly be sanctioned early.
CERTIFICTE:
Certified that I have personally Inspected the spot and prepared this estimate in a most economical and safe way executing the work.
Certified that I have personally Inspected the spot and got prepared this estimate in a most economical and safe way executing the work.
Abrstract:
#REF! |  |  | #REF!
#REF! |  |  | #REF!
#REF! |  |  | #REF!
| Total |  | #REF! |  | Say Rs | #REF! | /-Only
(Say Rupees Four lakhs Thirty Two thousand Nine Hundred and Three only)
CERTIFICTE:
Certified that I have personally Inspected the spot and prepared this estimate in a most economical
and safe way executing the work
Certified that I have personally Inspected the spot and prepared this estimate in a most economical
and safe way executing the work
Report:
This Estimate amounting to Rs. |  | #REF! | /-Only | has been prepared for |  | #REF!
#REF!
●In this estimate following proposals have been made.
●Extend 11 KV OH line for Twenty Four spans for a distance of 0.035 KM by and |  |  |  |  | #VALUE! | Kms using 9 Mtrs long
RCC/PSC poles and Rabbit ACSR Conductor as shown in the sketch.
● Provide a 25 KVA DTC using 9 Mtrs RCC DP Structure near near the IP set bearing RR No: SIP183 and 48097presently feeding from 63 KVA Chamundeshwari Temple DTC bearing DT code 523127
●Provide Road guarding, guy sets and stud pole wherever it is found essential.
The above said work shall be carried out under SELF EXECUTION, as per the request of the consumer
This additional DTC comes on F-1 Siddapur Feeder from 33/11KV MUSS Siddapur. HT voltage regulation of the said feeder has been calculated and the calculation chart and station feasibility reports are enclosed.
At present power supply to the said IP set installations are feeding from the existing 63 KVA Chamundeshwari Temple DTC and is getting low voltage during sprinkler season. hence the consumer has requested to provide a seperate transformer centre near his IP set and is ready to carryout the work under Self execution scheme.
All the necessary provision has been made in this estimate hence the estimate may kindly be sanctioned early.
CERTIFICTE:
Certified that I have personally Inspected the spot and prepared this estimate in a most economical and safe way executing the work.
Certified that I have personally Inspected the spot and got prepared this estimate in a most economical and safe way executing the work.
Estimate for providing |  | #REF!
#REF!
Index
Existing HT Pole 9/8 mtr RCC/PSC
Proposed Guy Set
Existing LT Line
Proposed LT Extension
Existing 11KV line
Proposed 63KVA dtc
Proposed 11KV Extension
Proposed RCC Pole 9 mtr
Proposed PSC Pole 9 mtr
Assistant Engineer(EL)
O&M Section Virajpet
Assistant Engineer(EL)
O&M Section Virajpet
Assistant Engineer(EL)
O&M Section Virajpet
Asst Executive Engineer(EL)
O&M Sub Division, Virajpet

## ltvr
CHAMUNDESHWARI ELECTRICITY SUPPLY CORPORATION LIMITED
LT Voltage regulation and Annual Energy Savings Calculation chart
For providing Additional 25KVA DTC to bifurcate the load of existing overloaded 25KVA B Shettigeri Panchayath (5242AB) DTC .
Name of the Section: | [6 empty] | VIRAJPET
Name of the Sub Division: | [6 empty] | VIRAJPET
DTC NAME: |  | B Shettigeri Panchayath, B Shettigeri Village | [5 empty] | DTC Code |  | 5242AB
a) Calculation for existing 25KVA B Shettigeri Panchayath (5242AB) DTC . (Existing)
LTVR | [7 empty] | ENERGY LOSS
Node No | Load at Node | Cummulative Load in HP |  | Km |  | Load x KM |  | Load2 |  | Km |  | Load2 X KM | Remarks
1 | 22.13 | 22.13 | × | 0.2 | = | 4.426 |  | 489.7369 | × | 0.2 | = | 97.9474
2 | 1.23 | 23.36 | × | 0.1 | = | 2.336 |  | 545.6896 | × | 0.1 | = | 54.569
3 | 0.54 | 23.9 | × | 0.1 | = | 2.39 |  | 571.21 | × | 0.1 | = | 57.121
4 | 0.43 | 24.33 | × | 0.05 | = | 1.2165 |  | 591.9489 | × | 0.05 | = | 29.5974
5 | 0.67 | 25 | × | 0.05 | = | 1.25 |  | 625 | × | 0.05 | = | 31.25
6 | 0.11 | 25.11 | × | 0.05 | = | 1.2555 |  | 630.5121 | × | 0.05 | = | 31.5256
7 | 4.83 | 29.94 | × | 0.05 | = | 1.497 |  | 896.4036 | × | 0.05 | = | 44.8202
8 | 0.32 | 30.26 | × | 0.25 | = | 7.565 |  | 915.6676 | × | 0.25 | = | 228.9169
9 | 2.68 | 32.94 | × | 0.05 | = | 1.647 |  | 1085.0436 | × | 0.05 | = | 54.2522
10 | 0.7 | 33.64 | × | 0.1 | = | 3.364 |  | 1131.6496 | × | 0.1 | = | 113.165
11 | 5.09 | 38.73 | × | 0.2 | = | 7.746 |  | 1500.0129 | × | 0.2 | = | 300.0026
12 | 2.12 | 40.85 | × | 0.05 | = | 2.0425 |  | 1668.7225 | × | 0.05 | = | 83.4361
13 | 2.68 | 43.53 | × | 0.1 | = | 4.353 |  | 1894.8609 | × | 0.1 | = | 189.4861
14 | 3.75 | 47.28 | × | 0.05 | = | 2.364 |  | 2235.3984 | × | 0.05 | = | 111.7699
15 | 1.34 | 48.62 | × | 0.05 | = | 2.431 |  | 2363.9044 | × | 0.05 | = | 118.1952
16 | 1.34 | 49.96 | × | 0.05 | = | 2.498 |  | 2496.0016 | × | 0.05 | = | 124.8001
17 | 4.02 | 53.98 | × | 0.05 | = | 2.699 |  | 2913.8404 | × | 0.05 | = | 145.692
18 | 3.32 | 57.3 | × | 0.2 | = | 11.46 |  | 3283.29 | × | 0.2 | = | 656.658
19 | 1.34 | 58.64 | × | 0.15 | = | 8.796 |  | 3438.6496 | × | 0.15 | = | 515.7974
20 | 2.68 | 61.32 | × | 0.05 | = | 3.066 |  | 3760.1424 | × | 0.05 | = | 188.0071
21 | 3.32 | 64.64 | × | 0.1 | = | 6.464 |  | 4178.3296 | × | 0.1 | = | 417.833
22 | 0.05 | 64.69 | × | 0.65 | = | 42.0485 |  | 4184.7961 | × | 0.65 | = | 2720.1175
23 | 0.05 | 64.74 | × | 0.8 | = | 51.792 |  | 4191.2676 | × | 0.8 | = | 3353.0141
24 | 0.05 | 40.9 | × | 0.05 | = | 2.045 |  | 1672.81 | × | 0.05 | = | 83.6405
Total | 64.79 | 1005.79 |  | 3.55 | Total | 176.752 | [5 empty] | 9751.6142
| % Regulation= |  | {(TotalKVA-Km)*Conductor constant}/100 |  |  |  |  | 9751.6142 | × | 0.093 | × | 8760
| % Regulation= |  | 111.2035 |  |  |  |  | Annual energy loss |  |  | 35308.6447 |  |  |  |  | 48.5925
[9 empty] | Assuming Diversity Factor |  |  |  | 1.5
a) Calculation for existing 25 KVA B Shettigeri Panchayath DTC (After bifurcation ) Residual
LTVR | [7 empty] | ENERGY LOSS
Node No | Load at Node | Cummulative Load in HP |  | Km |  | Load x KM |  | Load2 |  | Km |  | Load2 X KM | Remarks
1 | 7.9 | 7.9 | × | 0.1 | = | 0.79 |  | 62.41 | × | 0.1 | = | 6.241
2 | 3.75 | 11.65 | × | 0.05 | = | 0.5825 |  | 135.7225 | × | 0.05 | = | 6.7861
3 | 1.34 | 12.99 | × | 0.05 | = | 0.6495 |  | 168.7401 | × | 0.05 | = | 8.437
4 | 1.34 | 14.33 | × | 0.05 | = | 0.7165 |  | 205.3489 | × | 0.05 | = | 10.2674
5 | 4.02 | 18.35 | × | 0.05 | = | 0.9175 |  | 336.7225 | × | 0.05 | = | 16.8361
6 | 3.32 | 21.67 | × | 0.2 | = | 4.334 |  | 469.5889 | × | 0.2 | = | 93.9178
7 | 1.34 | 23.01 | × | 0.15 | = | 3.4515 |  | 529.4601 | × | 0.15 | = | 79.419
8 | 2.68 | 25.69 | × | 0.05 | = | 1.2845 |  | 659.9761 | × | 0.05 | = | 32.9988
9 | 3.32 | 29.01 | × | 0.1 | = | 2.901 |  | 841.5801 | × | 0.1 | = | 84.158
10 | 0.05 | 29.06 | × | 0.65 | = | 18.889 |  | 844.4836 | × | 0.65 | = | 548.9143
11 | 0.05 | 29.11 | × | 0.8 | = | 23.288 |  | 847.3921 | × | 0.8 | = | 677.9137
12 | 0.05 | 29.16 | × | 0.05 | = | 1.458 |  | 850.3056 | × | 0.05 | = | 42.5153
Total | 29.16 |  |  | 2.3 | Total | 59.262 | [5 empty] | 1608.4046 |  |  |  | 21.87
| % Regulation= |  | {(TotalKVA-Km)*Conductor constant}/100 |  |  |  |  | 1608.4046 | × | 0.093 | × | 8760
| % Regulation= |  | 37.2847 | [5 empty] | Annual energy loss |  |  | 5823.7114
Assuming Diversity factor 1.5
[10 empty] | Assuming Diversity Factor |  | 1.5
a) Calculation for Proposed Additional 25 KVA DTC
LTVR | [7 empty] | ENERGY LOSS
Node No | Load at Node | Cummulative Load in HP |  | Km |  | Load x KM |  | Load2 |  | Km |  | Load2 X KM | Remarks
1 | 14 | 14 | × | 0.2 | = | 2.8 |  | 196 | × | 0.2 | = | 39.2
2 | 1.23 | 15.23 | × | 0.1 | = | 1.523 |  | 231.9529 | × | 0.1 | = | 23.1953
3 | 0.54 | 15.77 | × | 0.1 | = | 1.577 |  | 248.6929 | × | 0.1 | = | 24.8693
4 | 0.43 | 16.2 | × | 0.05 | = | 0.81 |  | 262.44 | × | 0.05 | = | 13.122
5 | 0.67 | 16.87 | × | 0.05 | = | 0.8435 |  | 284.5969 | × | 0.05 | = | 14.2298
6 | 0.11 | 16.98 | × | 0.05 | = | 0.849 |  | 288.3204 | × | 0.05 | = | 14.416
7 | 4.83 | 21.81 | × | 0.05 | = | 1.0905 |  | 475.6761 | × | 0.05 | = | 23.7838
8 | 0.32 | 22.13 | × | 0.25 | = | 5.5325 |  | 489.7369 | × | 0.25 | = | 122.4342
9 | 2.68 | 24.81 | × | 0.05 | = | 1.2405 |  | 615.5361 | × | 0.05 | = | 30.7768
10 | 0.7 | 25.51 | × | 0.1 | = | 2.551 |  | 650.7601 | × | 0.1 | = | 65.076
11 | 5.09 | 30.6 | × | 0.2 | = | 6.12 |  | 936.36 | × | 0.2 | = | 187.272
12 | 2.12 | 32.72 | × | 0.05 | = | 1.636 |  | 1070.5984 | × | 0.05 | = | 53.5299
13 | 2.68 | 35.4 | × | 0.1 | = | 3.54 |  | 1253.16 | × | 0.1 | = | 125.316 |  | 64.79 | 64.56 | 0.23
Total | 35.4 |  |  | 1.35 | Total | 30.113 | [5 empty] | 737.2212 |  |  | 26.55
| % Regulation= |  | {(TotalKVA-Km)*Conductor constant}/100 |  |  |  |  | 737.2212 | × | 0.093 | × | 8760
| % Regulation= |  | 18.9456 | [5 empty] | Annual energy loss |  |  | 2669.3306
[10 empty] | Assuming Diversity Factor |  | 1.5
Assuming Diversity factor 1.5
Calculation of Annual Energy Savings | [8 empty] | Cost Benefit Ratio |  |  |  | Remarks
1 | Annual Energy losses before bifurcation (Existing DTC | [5 empty] | 35308.6447 |  | Estimate cost (In Rs) |  |  | 490458
2 | Annual Energy losses after bifurcation | [5 empty] | 5823.7114 |  | Cost per unit (In Rs) |  |  | 4.2
3 | Annual Energy losses of the proposed dtc | [5 empty] | 2669.3306 |  | Annual Savings (In Rs) |  |  | 112625.5316
4 | Annual energy savings in units | [5 empty] | 26815.6028 |  | Pay Back Period |  |  | 4.3548

## Load Details
63KVA MUKKOTI KOPPA TC DTC 524158 AMMATHI SECTION
SL.NO | Pole Number | RR.NO | DTC CODE | LOAD.KW | Load in HP | Total | Remarks
1 | 1 | 4360 | 524158 | 1 | 0
2 | 2 | A364 | 524158 | 0.1 | 0 | 0.1
3 | 2 | A381 | 524158 | 0.24 | 0
4 | 3 | A363 | 524158 | 0.46 | 0 | 0.46
5 | 3 | A365 | 524158 | 0.48 | 0
6 | 3 | A543 | 524158 | 0.36 | 0 | 0.36
7 | 3 | KRAEH16623 | 524158 | 1 | 0 | 1
8 | 3 | A366 | 524158 | 0.48 | 0 | 0.48
9 | 4 | A361 | 524158 | 0.48 | 0 | 0.48
10 | 4 | KRAEH21287 | 524158 | 0.36 | 0 | 0.36
11 | 5 | A375 | 524158 | 0.52 | 0 | 0.52
12 | 5 | A368 | 524158 | 0.48 | 0 | 0.48
13 | 5 | A316 | 524158 | 0.52 | 0 | 0.52
14 | 5 | A362 | 524158 | 0.48 | 0 | 0.48
15 | 5 | A542 | 524158 | 0.28 | 0 | 0.28
16 | 6 | A382 | 524158 | 0.52 | 0 | 0.52
17 | 6 | A367 | 524158 | 0.48 | 0 | 0.48
18 | 9 | 42447 | 524158 | 1 | 0 | 1
19 | 10 | KRL433 | 524158 | 0.24 | 0 | 0.24
20 | 11 | 422 | 524158 | 2 | 0 | 2
21 | 11 | KRAEH19915 | 524158 | 0.12 | 0 | 0.12
22 | 11 | KRL2345 | 524158 | 1 | 0 | 1
23 | 11 | KRAEH22647 | 524158 | 0.2 | 0 | 0.2
24 | 11 | KRAEH22648 | 524158 | 0.2 | 0 | 0.2
25 | 11 | KRAEH22649 | 524158 | 0.2 | 0 | 0.2
26 | 11 | A372 | 524158 | 0.48 | 0 | 0.48
27 | 12 | 40955 | 524158 | 0.6 | 0 | 0.6
28 | 12 | A373 | 524158 | 0.48 | 0 | 0.48
29 | 13 | 40216 | 524158 | 0.48 | 0 | 0.48
30 | 17 | 40504 | 524158 | 0.48 | 0 | 0.48
31 | 22 | GKSL34296 | 524158 | 2 | 0 | 2
32 | 23 | GKSL30577 | 524158 | 0.56 | 0 | 0.56
33 | 23 | AL21961 | 524158 | 0.48 | 0 | 0.48
34 | 24 | KRL21134 | 524158 | 0.4 | 0 | 0.4
35 | 24 | GKSL34292 | 524158 | 0.28 | 0 | 0.28
36 | 24 | GKSL34291 | 524158 | 0.28 | 0 | 0.28
37 | 24 | GKSL33840 | 524158 | 0.48 | 0 | 0.48
38 | 24 | KRL22131 | 524158 | 1 | 0 | 1
39 | 24 | AAEH16088 | 524158 | 0.48 | 0 | 0.48
40 | 24 | AAEH23788 | 524158 | 0.24 | 0 | 0.24
41 | 24 | AAEH23787 | 524158 | 0.24 | 0 | 0.24
42 | 24 | AAEH23793 | 524158 | 0.24 | 0 | 0.24
43 | 24 | AAEH23790 | 524158 | 0.24 | 0 | 0.24
44 | 24 | AAEH23789 | 524158 | 0.24 | 0 | 0.24
45 | 24 | AAEH23791 | 524158 | 0.24 | 0 | 0.24
46 | 25 | AAEH23792 | 524158 | 0.24 | 0 | 0.24
47 | 25 | A604 | 524158 | 0.32 | 0 | 0.32
48 | 26 | 40277 | 524158 | 3 | 0 | 3
49 | 26 | A182 | 524158 | 5 | 0 | 5
50 | 27 | AAEH21205 | 524158 | 0.2 | 0 | 0.2
51 | 28 | GKSL33387 | 524158 | 2 | 0 | 2
52 | 31 | GKSL31699 | 524158 | 0.24 | 0 | 0.24
53 | 32 | AAEH199 | 524158 | 1.64 | 0 | 1.64
54 | 33 | AAEH200 | 524158 | 1.97 | 0 | 1.97
55 | 34 | AAEH10783 | 524158 | 1 | 0 | 1
56 | 37 | A482 | 524158 | 0.28 | 0 | 0.28
57 | 37 | A481 | 524158 | 0.32 | 0 | 0.32
58 | 38 | A480 | 524158 | 0.32 | 0 | 0.32
59 | 38 | GKSL30737 | 524158 | 0.68 | 0 | 0.68
60 | 40 | GKSL33893 | 524158 | 0.48 | 0 | 0.48
61 | 43 | KRAEH24969 | 524158 | 0.24 | 0 | 0.24
62 | 44 | AAEH237 | 524158 | 1.48 | 0 | 1.48
63 | 63 | GKSL32224 | 524158 | 0.48 | 0 | 0.48
64 | 69 | HRAEH21783 | 524158 | 0.64 | 0 | 0.64
65 | 69 | HRAEH21782 | 524158 | 0.28 | 0 | 0.28
66 | 75 | KRIP2798 | 524158 |  | 10 | 7.46
67 | 75 | AAEH31 | 524158 | 2.4 | 0 | 2.4
68 | 75 | KRAEH18352 | 524158 | 2.4 | 0 | 2.4
69 | 75 | KRAEH18353 | 524158 | 0.24 | 0 | 0.24
70 | 75 | KRAEH18351 | 524158 | 0.24 | 0 | 0.24
71 | 76 | AAEH118 | 524158 | 3 | 0 | 3
72 | 82 | A94 | 524158 | 0.24 | 0 | 0.24
73 | 86 | GKSL32524 | 524158 | 1.79 | 0 | 1.79
74 | 87 | AAEH188 | 524158 | 2.8 | 0 | 2.8
75 | 98 | AAEH24639 | 524158 | 0.52 | 0 | 0.52
76 | 102 | SP1326 | 524158 | 0 | 5 | 3.73
77 | 104 | KRIP2642 | 524158 | 0 | 7.5 | 5.595
78 | 104 | GKSIP3656 | 524158 | 0 | 10 | 7.46
79 | 105 | GKSIP3759 | 524158 | 0 | 20 | 14.92
80 | 106 | GKSIP3240 | 524158 | 0 | 10 | 7.46
TOTAL |  |  |  | 56.56 | 62.5 | 102.465

## Sheet1
ATC Losses MD Meeting notes Dt:25.4.2017
INDEX
Sl.no | Perticulars | Page Number
1 | Monthwise Feederwise Energy Audit Comparision Statement | 1 to 14
2 | Siddapura 11KV feeders energy Calculation | 15
3 | R format of Virajpet Subdivision | 16 to 20
4 | Tarriff wise MNR,DC,DL Zero Consumption reports for the month of March 2017 | 21
5 | MNR Statement | 22
6 | Long disconnected installation | 23
7 | details of Pending test report | 24
8 | Meter readerwise Billing Effeciency | 25
9 | Solar rebate Details | 26
10 | Tax exempted Details | 27
11 | Pending Govt arrears for the month of March 2017 | 28
12 | Disconnection Details | 29

## Sheet2
Estimate for providing |  | #REF!
#REF!
Index
Existing HT Pole 9/8 mtr RCC/PSC
Proposed Guy Set
Existing LT Line
Proposed LT Extension
Existing 11KV HT line Gonikoppa Feeder
Proposed 63KVA dtc
Proposed 11KV Extension
Proposed RCC Pole 9 mtr
Proposed PSC Pole 9 mtr
Proposed 63 KVA DTC
35m
Junior Engineer(EL)
O&M Section Siddapura
Asst Executive Engineer(EL)
O&M Sub Division, Virajpet
35m
35m
35m
35m
Existing 100 kva transformer
Existing 100 kva transformer

## Sheet3
|  | Node point load | Distance
1
2
3
4 |  | 16.51 | 0.2 | 22.1314 | hp | kw
5 | 1.48 |  |  | 0
6 | 2.2 |  |  | 0
7 | 0.4 |  |  | 0
8 |  |  |  | 0
9 | 2.27 |  |  | 0
10 |  |  |  | 0
11 |  |  |  | 0
12 |  |  |  | 0
13 | 3.48 |  |  | 0
14 | 2.48 |  |  | 0
15 |  |  |  | 0
16 | 1.8 |  |  | 0
17 | 2 |  |  | 0
18 | 0.4 |  |  | 0
19 |  |  |  | 0
20 |  | 0.92 | 0.1 | 1.2332
21 | 0.92 |  |  | 0
22 | 0.4 | 0.4 | 0.1 | 0.53619
23 |  |  |  | 0
24 | 0.32 | 0.32 | 0.05 | 0.42895
25 |  | 0.5 | 0.05 | 0.67024
26 |  |  |  | 0
27 |  |  |  | 0
28 | 0.5 |  |  | 0
29 |  | 0.08 | 0.05 | 0.10724
30 |  |  |  | 0
31 |  |  |  | 0
32 |  |  |  | 0
33 |  |  |  | 0
34 |  |  |  | 0
35 | 0.08 |  |  | 0
36 | 3.6 | 3.6 | 0.05 | 4.8257
37 |  |  |  | 0
38 |  |  |  | 0
39 |  |  |  | 0
40 | 0.24 | 0.24 | 0.25 | 0.32172
41 |  | 2 | 0.05 | 2.681
42 |  |  |  | 0
43 |  |  |  | 0
44 |  |  |  | 0
45 |  |  |  | 0
46 |  |  |  | 0
47 |  |  |  | 0
48 |  |  |  | 0
49 | 2 |  |  | 0
50 |  |  |  | 0
51 | 0.52 | 0.52 | 0.1 | 0.69705
52 |  |  |  | 0
53 |  |  |  | 0
54 |  |  |  | 0
55 | 3.8 | 3.8 | 0.2 | 5.0938
56 |  |  |  | 0
57 | 1.58 | 1.58 | 0.05 | 2.118
58 |  |  |  | 0
59 | 2 | 2 | 0.1 | 2.681
60 | 2.8 | 2.8 | 0.05 | 3.7534
61 | 1 | 1 | 0.05 | 1.3405
62 | 1 | 1 | 0.05 | 1.3405
63 | 3 | 3 | 0.05 | 4.0214
64 |  |  |  | 0
65 |  |  |  | 0
66 |  |  |  | 0
67 | 2.48 | 2.48 | 0.2 | 3.3244
68 |  |  |  | 0
69 |  |  |  | 0
70 | 1 | 1 | 0.15 | 1.3405
71 | 2 | 2 | 0.05 | 2.681
72 |  |  |  | 0
73 | 2 | 2.48 | 0.1 | 3.3244
74 |  |  |  | 0
75 |  |  |  | 0
76 |  |  |  | 0
77 |  |  |  | 0
78 | 0.48 |  |  | 0
79 |  |  |  | 0
80 |  |  |  | 0
81 |  |  |  | 0
82 |  |  |  | 0
83 |  |  |  | 0
84 |  |  |  | 0
85 |  |  |  | 0
86 | 0.04 | 0.04 | 0.65 | 0.053619
87 |  |  |  | 0
88 |  |  |  | 0
89 |  |  |  | 0
90 |  |  |  | 0
91 |  |  |  | 0
92 |  |  |  | 0
93 |  |  |  | 0
94 |  |  |  | 0
95 |  |  |  | 0
96 |  |  |  | 0
97 |  |  |  | 0
98 |  |  |  | 0
99 |  |  |  | 0
100 |  |  |  | 0
101 |  |  |  | 0
102 | 0.04 | 0.04 | 0.8 | 0.053619
103 | 0.04 | 0.04 | 0.05 | 0.053619